## ΔP Calculator
PRESSURE DROP CALCULATOR
Project:
Date:
| Pipe length: |  | 170 | m
| Specific Gravity: |  | 0.848
| Dynamic Viscosity: |  | 0.36 | cP
| Flow Q: |  | 100 | m3/hr
| Pipe inner surface roughnes |  | 0.04 | mm
| Inside diameter: |  | 154 | mm
| No. of 900 Elbows: |  | 60
| Equivalent Length (30xD)L90: |  | 277.2 | m
| No. of 450C elbows |  | 1
| Equivalent Length (16 x D) L45: |  | 2.464 | m
| No. of Gate Valves Fully opened: |  | 0
| Equivalent Length (13 x D) LV |  | 0 | m
| No. of Globe Valves Fully opened: |  | 0
| Equivalent Length (340 x D) LV |  | 0 | m
| Ball Valve RB, > DN 50 |  | 0
| Equivalent Length (45 x D) Lb |  | 0 | m
| Swing Type NRV |  | 0
| Equivalent length (135 x D)LNRV |  | 0 | m
| No. of Y-Type Strainers: |  | 0
| Y Strainer Equivalent Length LY Length (250 x D) |  | 0 | m
| No. of "T" Flow straight through |  | 0
| Equivalent Length (20 x D) LST |  | 0 | m
| No. of "T" Flow through side outlet |  | 0
| Equivalent Length (65 x D) LTS |  | 0 | m
| Product outlet nozzle vessel/tank |  | 0
| Equivalent length (32 x D) LIN |  | 0 | m
| Product outlet nozzle vessel/tank |  | 0
| Equivalent length (64 x D) LOUT |  | 0 | m
| Change in Elevation: |  | 0 | m
| Tank Height: |  | 0 | m
| Fluid Velocity V (Should not exceed 5 m/s): |  | 1.4913 | m/s
| Reynold's Number (Re): |  | 540978.8029
Flow is Turbulent
| Total Equivalent Length |  | 449.664 | m
| ε/D= |  | 0.00025974
| Additional Static Equipment Pressure Drop |  | 1 | Bar
| Friction factor (f): |  | 0.015859
| Pressure Drop: |  | 1.4366 | Bar
| Head Loss: |  | 17.2697 | meters
To be entered manually
GVL Management & Consulting Ltd
P.O.Box 42286, 6532, Larnaca, CYPRUS, E-mail: george@gvlengineering.com
| A= | 8.0688
| B= | 7.9361
| C= | 7.9411 | 0.011652
7.9409
| f= | 0.015859
0.015859